## PV
Description | code | type | cap_min | cap_max | unit | module_length_m | PV_th | PV_n | PV_noct | PV_Bref | PV_a0 | PV_a1 | PV_a2 | PV_a3 | PV_a4 | misc_losses | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic monocrystalline panel | PV1 | PV | 1 | 10000 | W | 1 | 0.002 | 0.16 | 43.5 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic monocrystalline panel | PV1 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.16 | 43.5 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic monocrystalline panel | PV1 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.16 | 43.5 | 0.0035 | 0.93582 | 0.054289 | 0.008677 | 0.000527 | -1.1e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity
generic polycrystalline panel | PV2 | PV | 1 | 10000 | W | 1 | 0.002 | 0.15 | 43.9 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic polycrystalline panel | PV2 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.15 | 43.9 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic polycrystalline panel | PV2 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.15 | 43.9 | 0.0044 | 0.91809 | 0.086257 | -0.024459 | 0.002816 | -0.000126 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity
generic amorphous silicon panel | PV3 | PV | 1 | 10000 | W | 1 | 0.002 | 0.08 | 38.1 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 3.6383 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic amorphous silicon panel | PV3 | PV | 10000 | 200000 | W | 1 | 0.002 | 0.08 | 38.1 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%
generic amorphous silicon panel | PV3 | PV | 200000 | 10000000000 | W | 1 | 0.002 | 0.08 | 38.1 | 0.0026 | 1.1004 | -0.061423 | -0.0044273 | 0.0006315 | -1.9184e-05 | 0.1 | USD-2015 | 0 | 2.5988 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%, capacity

## SC
Description | code | type | module_length_m | module_area_m2 | aperture_area_ratio | n0 | c1 | c2 | mB0_r | mB_max_r | mB_min_r | C_eff | t_max | IAM_d | dP1 | dP2 | dP3 | dP4 | Cp_fluid | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
flat plate | SC1 | FP | 2 | 2.023 | 0.888 | 0.775 | 3.91 | 0.0081 | 57.98 | 86.97 | 28.99 | 8000 | 192 | 0.87 | 0 | 94.6324 | 150.2986 | 44.5329 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2130.9771 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%
evacuated tube | SC2 | ET | 2 | 4.322 | 0.655 | 0.721 | 0.89 | 0.0199 | 88.2 | 147.12 | 33.1 | 39000 | 196 | 0.91 | 0 | 2825.9464 | 7771.3527 | 706.4866 | 3680 | 1 | 10000000000 | m2 | USD-2015 | 0 | 2130.9771 | 1 | 0 | 0 | 20 | 5 | 5 | IR_%

## PVT
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic PVT | PVT1 | 1 | 10000000000 | W | USD-2015 | 0 | 5.1975 | 1 | 0 | 0 | 20 | 1 | 5 | IR_%

## Boiler
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
condensing boiler | BO1 | 28000 | 90000 | W | USD-2015 | 22505.5432 | 0.30488 | 1 | 0 | 0 | 20 | 5 | 5
condensing boiler | BO1 | 90000 | 320000 | W | USD-2015 | 38913.5255 | 0.12195 | 1 | 0 | 0 | 20 | 5 | 5
condensing boiler | BO1 | 320000 | 10000000000 | W | USD-2015 | 93126.3858 | 0.015521 | 1 | 0 | 0 | 20 | 5 | 5

## Furnace
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
furnace combined with ORC | FU1 | 1000000 | 10000000 | W | USD-2015 | 0 | 0.74279 | 1 | 0 | 0 | 20 | 5 | 5

## FC
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | Assumptions
solid oxide fuel cell | FC1 | 1000 | 10000 | W | USD-2015 | 0 | 13.7214 | 1 | 0 | 0 | 10 | 5 | 5
solid oxide fuel cell | FC1 | 10000 | 10000000000 | W | USD-2015 | 0 | 13.7214 | 1 | 0 | 0 | 10 | 5 | 5 | all

## CCGT
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
combined cycle gas turbine | CCGT1 | 1 | 10000000000 | W | USD-2015 | 0 | 555.8316 | 0.5967 | 0 | 0 | 25 | 3 | 6

## Chiller
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
centralized chiller | CH1 | 1000000 | 3500000 | W | USD-2015 | 0 | 0.43025 | 0.6 | 0 | 0 | 25 | 5 | 5 | IR_%
vapor compression chiller | CH2 | 1 | 10000000000 | W | USD-2015 | 12590.9091 | 0.14135 | 1 | 0 | 0 | 25 | 5 | 5 | IR_%
vapor compression chiller | CH3 | 1 | 10000000000 | W | USD-2015 | 0 | 0.36063 | 1 | 0 | 0 | 25 | 5 | 5

## CT
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
centralized cooling tower | CT1 | 1 | 10000000 | W | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 15 | O&M_%
centralized cooling tower | CT1 | 10000000 | 10000000000000000 | W | USD-2015 | 1457.3 | 0.0161 | 1 | 0 | 0 | 20 | 5 | 15 | all

## HEX
Description | code | cap_min | cap_max | unit | Currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
substation heat exchanger | HEX1 | 50000 | 80000 | W | USD-2015 | -346.1538 | 0.069647 | 1 | 0 | 0 | 20 | 5 | 5
substation heat exchanger | HEX1 | 80000 | 100000 | W | USD-2015 | 5197.5052 | 0 | 0 | 0 | 0 | 20 | 5 | 5
substation heat exchanger | HEX1 | 100000 | 10000000000 | W | USD-2015 | -3118.5031 | 0.08316 | 1 | 0 | 0 | 20 | 5 | 5

## BH
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
borehole | BH1 | 1 | 10000000000 | W | USD-2015 | 0 | 47.4279 | 0.74 | 0 | 0 | 50 | 0 | 5

## HP
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
geothermal heat pump | HP1 | 1 | 10000000000 | W | USD-2015 | 0 | 197.1175 | 0.49 | 0 | 0 | 20 | 0 | 5
water-water heat pump | HP2 | 1000000 | 20000000 | W | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6
water-water heat pump | HP2 | 20000000 | 20000000000000000 | W | USD-2015 | 0 | 9.8592 | 1 | 0 | -0.54715 | 25 | 5 | 6 | all

## Pump
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
generic pump | PU1 | 500 | 4000 | W | USD-2015 | 0 | 29.3139 | 0.5216 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 4000 | 37000 | W | USD-2015 | 0 | 4.323 | 0.7464 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 37000 | 375000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | LT_yr
generic pump | PU1 | 375000 | 10000000000 | W | USD-2015 | 0 | 1.0168 | 0.8873 | 0 | 0 | 25 | 1 | 6 | all

## TES
Description | code | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption
long-term storage tank | TES1 | 100 | 12000 | m3 | USD-2015 | 0 | 2880.6653 | 1 | 0 | -295.4262 | 25 | 1 | 6 | cap_min, cap_max
long-term storage tank | TES1 | 12000 | 10000000000 | m3 | USD-2015 | 0 | 2880.6653 | 1 | 0 | -295.4262 | 25 | 1 | 6 | cap_max
short-term storage tank | TES2 | 0 | 10000000000 | m3 | USD-2015 | 0 | 699.4741 | 1 | 0 | 0 | 25 | 1 | 6 | cap_min, cap_max

## Pricing
Description | currency | value | assumption
ng_price | EURO | 6.8e-05
bg_price | EURO | 7.6e-05
ng_price_zernez | EURO | 7.56e-05
bg_price_zernez | EURO | 0.000162
elec_price | EURO | 0.0002
cpump | EURO | 1.752
cc_maintenance_per_kWhel | EURO | 0.03
euro_to_chf |  | 1.2
usd_to_chf |  | 0.96
mwst |  | 0.08

## Piping
Description | Diameter_max | Diameter_min | Unit | Investment | Currency | assumption
DN1500 | 1500 | 1400 | mm | 3234.4235 | USD-2015 | extrapolated
DN1400 | 1400 | 1300 | mm | 2936.1902 | USD-2015 | extrapolated
DN1300 | 1300 | 1200 | mm | 2642.2886 | USD-2015 | extrapolated
DN1200 | 1200 | 1100 | mm | 2310.1445 | USD-2015
DN1100 | 1100 | 1000 | mm | 2075.2539 | USD-2015 | extrapolated
DN1000 | 1000 | 900 | mm | 1911.5018 | USD-2015
DN900 | 900 | 800 | mm | 1596.929 | USD-2015
DN800 | 800 | 700 | mm | 1209.7253 | USD-2015
DN700 | 700 | 600 | mm | 1060.7673 | USD-2015
DN600 | 600 | 500 | mm | 814.5945 | USD-2015
DN500 | 500 | 450 | mm | 683.5644 | USD-2015
DN450 | 450 | 400 | mm | 591.467 | USD-2015
DN400 | 400 | 350 | mm | 537.7003 | USD-2015
DN350 | 350 | 300 | mm | 468.3304 | USD-2015
DN300 | 300 | 250 | mm | 383.9928 | USD-2015
DN250 | 250 | 200 | mm | 309.9235 | USD-2015
DN200 | 200 | 150 | mm | 248.9155 | USD-2015
DN150 | 150 | 125 | mm | 203.4772 | USD-2015
DN125 | 125 | 100 | mm | 189.5965 | USD-2015
DN100 | 100 | 80 | mm | 155.8481 | USD-2015
DN80 | 80 | 65 | mm | 146.1618 | USD-2015 | extrapolated
DN65 | 65 | 50 | mm | 136.0147 | USD-2015 | extrapolated
DN50 | 50 | 40 | mm | 126.5488 | USD-2015 | extrapolated
DN40 | 40 | 32 | mm | 120.6199 | USD-2015 | extrapolated
DN32 | 32 | 25 | mm | 116.0982 | USD-2015 | extrapolated
DN25 | 25 | 20 | mm | 112.304 | USD-2015 | extrapolated
DN20 | 20 | 0 | mm | 109.6869 | USD-2015 | extrapolated

## Absorption_chiller
Description | code | type | cap_min | cap_max | unit | currency | a | b | c | d | e | LT_yr | O&M_% | IR_% | assumption | el_W | s_e | r_e | s_g | r_g | a_e | e_e | a_g | e_g | m_cw | m_hw
LiBr single effect | ACH1 | single | 0 | 51150 | W | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 5 | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 0.722 | 0.333
LiBr single effect | ACH2 | single | 51150 | 1176000 | W | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 5.7 | 68.12 | -3281.1 | 88.05 | -4216.1 | -1.45 | 1.75 | -1.45 | 1.75 | 81 | 33
LiBr single effect | ACH2 | single | 1176000 | 10000000000 | W | USD-2015 | 0 | 0.4395 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 5.7 | 68.12 | -3281.1 | 88.05 | -4216.1 | -1.45 | 1.75 | -1.45 | 1.75 | 81 | 33
LiBr double effect (dummy) | ACH3 | double | 0 | 58150 | W | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 5 | 0.42 | 0.9 | 0.53 | -2.5 | -2.5 | 1.8 | -2.1 | 1.5 | 0.722 | 0.333
LiBr double effect | ACH4 | double | 58150 | 1337450 | W | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 6.8 | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 68 | 14
LiBr double effect | ACH4 | double | 1337450 | 10000000000 | W | USD-2015 | 0 | 0.5297 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 6.8 | 18.1 | -1350.5 | 12.54 | -917.3 | -2.46 | 4.38 | -2.46 | 4.38 | 68 | 14
LiBr triple effect | ACH5 | triple | 116300 | 1628200 | W | USD-2015 | 0 | 0.6424 | 1 | 0 | 0 | 25 | 5 | 5 | IR_% | 6.55 | 14.6 | -1171.7 | 7.05 | -504.2 | -2.14 | 3.29 | -2.14 | 3.29 | 62 | 10